Problem 1: Heating of Process Stream (Sensible Heat Duty)

Problem Statement

A liquid stream of 10,000 lb/hr is heated from 80°F to 150°F in a heat exchanger. The specific heat capacity of the liquid is approximately cp = 0.95 Btu/lb-°F. Calculate the heat duty required (Btu/hr) and also express the heat duty in kW.
Use 1 kW = 3412 Btu/hr.

Solution (Step-by-Step)

Step 1: Temperature rise

ΔT = 150 − 80 = 70°F

Step 2: Sensible heat duty

Q = m cp ΔT

Q = 10,000 × 0.95 × 70

Q = 10,000 × 66.5 = 665,000 Btu/hr

Step 3: Convert to kW

Q(kW) = Q(Btu/hr) / 3412

Q(kW) = 665,000 / 3412 = 194.9 kW

Final Answer

Heat duty Q ≈ 665,000 Btu/hr ≈ 195 kW.

Problem 2: LMTD Heat Exchanger Sizing (Counterflow)

Problem Statement

Hot oil is cooled from 260°F to 180°F in a counterflow heat exchanger. Cooling water enters at 70°F and leaves at 110°F. The overall heat transfer coefficient is U = 120 Btu/hr-ft²-°F. The heat duty is Q = 1.2×10^6 Btu/hr. Determine the required heat transfer area A (ft²).

Solution (Step-by-Step)

Step 1: Temperature differences for counterflow

ΔT1 = Th,in − Tc,out = 260 − 110 = 150°F

ΔT2 = Th,out − Tc,in = 180 − 70 = 110°F

Step 2: LMTD

LMTD = (ΔT1 − ΔT2)/ln(ΔT1/ΔT2)

= (150 − 110)/ln(150/110)

= 40/ln(1.3636)

ln(1.3636)=0.310

LMTD ≈ 40/0.310 = 129.0°F

Step 3: Heat exchanger area

Q = U A (LMTD)

A = Q/(U×LMTD)

A = 1.2×10^6 / (120×129.0)

Denominator = 15,480

A ≈ 77.5 ft²

Final Answer

Required heat transfer area A ≈ 77.5 ft².

Problem 3: Boiler Efficiency and Fuel Requirement

Problem Statement

A process requires 8,000 lb/hr of saturated steam at 100 psig. Feedwater enters the boiler at 60°F. Assume enthalpy of saturated steam at 100 psig is approximately hg = 1190 Btu/lb and feedwater enthalpy is hf,60°F ≈ 28 Btu/lb. The boiler efficiency is 80%. Fuel has heating value of 20,000 Btu/lb.
Determine:
1) Useful heat added to water (Btu/hr)
2) Fuel heat input required (Btu/hr)
3) Fuel consumption rate (lb/hr).

Solution (Step-by-Step)

Step 1: Useful heat per lb of steam

Δh = hg − hf = 1190 − 28 = 1162 Btu/lb

Step 2: Useful heat rate

Q_useful = m_steam × Δh

Q_useful = 8000 × 1162 = 9,296,000 Btu/hr

Step 3: Fuel heat input using efficiency

η = Q_useful / Q_fuel

Q_fuel = Q_useful / η = 9,296,000 / 0.80

Q_fuel = 11,620,000 Btu/hr

Step 4: Fuel consumption

m_fuel = Q_fuel / HV

m_fuel = 11,620,000 / 20,000 = 581 lb/hr

Final Answer

Useful heat ≈ 9.30×10^6 Btu/hr.
Fuel heat input ≈ 1.162×10^7 Btu/hr.
Fuel consumption ≈ 581 lb/hr.